ION7300.SNF (Modified)

//Format:

//Axxxxx=Name

//A represents an analog measurement.

//xxxxx is the Code number in PecConfig. It is defined by the driver. For ION meters, xxxxx is the correspond ION Handle in decimal, except from 1 to 31.

//Name is the name of the measurement.

//Black: Not changed

//Red: The Code number is changed

//I4, V4, I5 Harmonics are not supported by ION7300. So the registers are deleted.

//Blue: Not changed. Need to check the ION module # of the registers from the ION7300 meter.

A0=Vlnavg

A1=Va

A2=Vb

A3=Vc

A4=Vllavg

A5=Vab

A6=Vbc

A7=Vca

A8=Iavg

A9=Ia

A10=Ib

A11=Ic

A12=I4

A13=V Unbalance

A14=I Unbalance

A15=kW Total

A16=kWa

A17=kWb

A18=kWc

A19=kVAR Total

A20=kVARa

A21=kVARb

A22=kVARc

A23=kVA Total

A24=kVAa

A25=kVAb

A26=kVAc

A27=PF Total

A28=PFa

A29=PFb

A30=PFc

A31=Frequency

A22704=kWh Import

A22705=kWh Export

A22706=kWh Total

A22707=kWh Net

A22708=kVARh Import

A22709=kVARh Export

A22710=kVARh Total

A22711=kVARh Net

A22712=kVAh Total

A22784=Va HD01

A22785=Va HD02

A22786=Va HD03

A22787=Va HD04

A22788=Va HD05

A22789=Va HD06

A22790=Va HD07

A22791=Va HD08

A22792=Va HD09

A22793=Va HD10

A22794=Va HD11

A22795=Va HD12

A22796=Va HD13

A22797=Va HD14

A22798=Va HD15

A22847=Va THD

A22848=Va TEHD

A22849=Va TOHD

A22850=Vb HD01

A22851=Vb HD02

A22852=Vb HD03

A22853=Vb HD04

A22854=Vb HD05

A22855=Vb HD06

A22856=Vb HD07

A22857=Vb HD08

A22858=Vb HD09

A22859=Vb HD10

A22860=Vb HD11

A22861=Vb HD12

A22862=Vb HD13

A22863=Vb HD14

A22864=Vb HD15

A22913=Vb THD

A22914=Vb TEHD

A22915=Vb TOHD

A22916=Vc HD01

A22917=Vc HD02

A22918=Vc HD03

A22919=Vc HD04

A22920=Vc HD05

A22921=Vc HD06

A22922=Vc HD07

A22923=Vc HD08

A22924=Vc HD09

A22925=Vc HD10

A22926=Vc HD11

A22927=Vc HD12

A22928=Vc HD13

A22929=Vc HD14

A22930=Vc HD15

A22979=Vc THD

A22980=Vc TEHD

A22981=Vc TOHD

A22982=Ia HD01

A22983=Ia HD02

A22984=Ia HD03

A22985=Ia HD04

A22986=Ia HD05

A22987=Ia HD06

A22988=Ia HD07

A22989=Ia HD08

A22990=Ia HD09

A22991=Ia HD10

A22992=Ia HD11

A22993=Ia HD12

A22994=Ia HD13

A22995=Ia HD14

A22996=Ia HD15

A23045=Ia THD

A23046=Ia TEHD

A23047=Ia TOHD

A23049=Ib HD01

A23050=Ib HD02

A23051=Ib HD03

A23052=Ib HD04

A23053=Ib HD05

A23054=Ib HD06

A23055=Ib HD07

A23056=Ib HD08

A23057=Ib HD09

A23058=Ib HD10

A23059=Ib HD11

A23060=Ib HD12

A23061=Ib HD13

A23062=Ib HD14

A23063=Ib HD15

A23112=Ib THD

A23113=Ib TEHD

A23114=Ib TOHD

A23116=Ic HD01

A23117=Ic HD02

A23118=Ic HD03

A23119=Ic HD04

A23120=Ic HD05

A23121=Ic HD06

A23122=Ic HD07

A23123=Ic HD08

A23124=Ic HD09

A23125=Ic HD10

A23126=Ic HD11

A23127=Ic HD12

A23128=Ic HD13

A23129=Ic HD14

A23130=Ic HD15

A23179=Ic THD

A23180=Ic TEHD

A23181=Ic TOHD

A22656=kW Total Demand

A22657=kVAR Total Demand

A22658=kVA Total Demand

A22659=Iavg Demand

A22778=kW Total Peak Demand

A22779=kVAR Total Peak Demand

A22780=kVA Total Peak Demand

How to change the ION7300 configurations using PecConfig

Change the ION7300 configurations one by one manually. Please do not use the Import SNF file method, otherwise, the data have to be relinked in PecDraw .

For example, the Property_Services_Main device(ION7300):

1) Click the mouse for twice in the Code cell of kVAh Total, change from 22714 to 22712.

Change the Code of Va THD and downwards to Ic TOHD according to the modified SNF file.

2) Press Shift and select from I4 HD01 to I5 TOHD and click Delete from the toolbar to delete them.

3) Check the ION Handle # of the SWinDemand modules and the Maximum modules of the sliding window demand and peak demand parameters.

4) Change the configurations of all other ION7300 meter in the same way.