Technical Note

Subject: How to Find Out the Available Depth for the Data Recorder in PMC-630B&C, PMC-660

(* For PMC-680i, the depth is fixed to be 12800. Therefore, we’ll not discuss here.)

The formula to obtain the available depth of Data Recorder is as follows –

Remarks:

1. Depth: For both PMC-630B&C and PMC-660, the maximum depth should be equal to or less than

65535, i.e. the maximum allowable setup value.

2. Memory Capacity: the total memory available for data logging, disregarding the necessary memory

reserved for fundamental log structure.

a. For PMC-630C, the total memory is 2048KB, and 2040KB is available.

b. For PMC-660, the total memory is 4096KB, and 3936KB is available. The unit of each recorder

is 1KB.

3. # of Parameters: the number of parameters that will be logged

4. Parameter Size in Byte: For all PMC meters, any parameter will require 4 bytes to be stored in data

log.

5. Timestamp Size:

A corresponding timestamp will also be recorded at recording a parameter.

a. For PMC-630C, the Timestamp will require 6 bytes.

b. For PMC-660, the Timestamp will require 8 bytes. The two extra bytes are used for msec.

The above formula is applicable for PMC-630B&C, PMC-660.

Example 1:

You have a PMC-630C which has 2MB of memory for data logging.

Specification for PMC-630C’s Data Recorders:

16 Data Recorder Logs of 16 parameters each for real-time measurements

Recording interval from 1s to 40 days

Configurable depths and recording offsets

2MB log memory

If you only want to log 3 parameters – Va, Vb & Vc with logging interval of 1 second, then this is the way to calculate the depth you’ll get –

Since this value is greater than 65535, you can only log 65535 records.

Example 2:

You have a PMC-660 which has 4MB of memory for data logging.

Specification for PMC-660’s Data Recorders:

- 12 standard Data Recorder Logs

- 4 high‐speed Data Recorder Logs (1 cycle interval)

- Recording interval from 1s to 40 days for standard and 1 to 60 cycles

- for high‐speed

- Programmable sources include almost all real‐time, harmonics,

- unbalance and demand values

- Configurable depth and recording offset

- Support FIFO or stop‐when‐full recording mode

If you want to log 20 parameters with logging interval of 15 minutes, then

this is the way to calculate the depth you’ll get –

Which means you can log up to 45800 records.