Technical Note

Subject: How to Evaluate the Memory Size Growth of PecStar_Data Database

The PecStar iEMS database contains PecStar_Config and PecStar_Data.

The PecStar_Data database mainly stores datalog (including meter datalog, virtual datalog, report datalog, energy datalog), SOE and waveform.

- The formula to obtain the memory size growth of Report Data is as follows –

Growth (MB) =

136 x #of Device x #of Group x 60 x 24 x Running Days

Interval x (1024 x 1024)

Remarks:

- Each recorder for one group of report data points requires 136 bytes.

| PD_TB_13_YYYY_MM_StationID: Report Data |  |  |  |  |
| --- | --- | --- | --- | --- |
| Column Name | Data Type | Data Length (Byte) | Allow Nulls | Description |
| DaymeasStartID | int | 4 |  | The start ID of Report Data Point of the group |
| Logtime | smalldatetime | 4 |  | The Log time of Report Data Point of the group |
| val1 | float | 8 | Y | The Real-time value for the 1st Report Data Point in the group |
| val2 | float | 8 | Y | The Real-time value for the 2nd Report Data Point in the group |
| val3 | float | 8 | Y | The Real-time value for the 3rd Report Data Point in the group |
| val4 | float | 8 | Y | The Real-time value for the 4th Report Data Point in the group |
| val5 | float | 8 | Y | The Real-time value for the 5th Report Data Point in the group |
| val6 | float | 8 | Y | The Real-time value for the 6th Report Data Point in the group |
| val7 | float | 8 | Y | The Real-time value for the 7th Report Data Point in the group |
| val8 | float | 8 | Y | The Real-time value for the 8th Report Data Point in the group |
| val9 | float | 8 | Y | The Real-time value for the 9th Report Data Point in the group |
| val10 | float | 8 | Y | The Real-time value for the 10th Report Data Point in the group |
| val11 | float | 8 | Y | The Real-time value for the 11th Report Data Point in the group |
| val12 | float | 8 | Y | The Real-time value for the 12th Report Data Point in the group |
| val13 | float | 8 | Y | The Real-time value for the 13th Report Data Point in the group |
| val14 | float | 8 | Y | The Real-time value for the 14th Report Data Point in the group |
| val15 | float | 8 | Y | The Real-time value for the 15th Report Data Point in the group |
| val16 | float | 8 | Y | The Real-time value for the 16th Report Data Point in the group |
| Total |  | 136 |  |  |

- #of Group = Ceiling (# of Report Data Points / 16). Each group consists of 16 report data points. For example, if there are 30 report data points, data point 1~16 will be in group 1, and data point 17~30 will be in group 2.

- Interval is in minutes.

- One report data stores for 365 days, at a 5-minute interval, will approximately consume 1MB size.

- The formula to obtain the memory size growth of Meter/Virtual Datalog is as follows –

Growth (MB) =

143 x #of Device x #of Group x 60 x 24 x Running Days

Interval x (1024 x 1024)

Remarks:

- Each group of meter/virtual datalog requires 143 bytes.

| PD_TB_01_YYYY_MM_StationID: Datalog |  |  |  |  |
| --- | --- | --- | --- | --- |
| Column Name | Data Type | Data Length (Byte) | Allow Nulls | Description |
| SourceID | int | 4 |  | Data Recorder ID |
| LogTime | datetime | 8 |  | Data Recoder LogTime |
| Msec | int | 2 |  | Data Recoder LogTime（millisecond） |
| Data1 | float | 8 | Y | The 1st value of the Data Recorder |
| Data2 | float | 8 | Y | The 2nd value of the Data Recorder |
| Data3 | float | 8 | Y | The 3rd value of the Data Recorder |
| Data4 | float | 8 | Y | The 4th value of the Data Recorder |
| Data5 | float | 8 | Y | The 5th value of the Data Recorder |
| Data6 | float | 8 | Y | The 6th value of the Data Recorder |
| Data7 | float | 8 | Y | The 7th value of the Data Recorder |
| Data8 | float | 8 | Y | The 8th value of the Data Recorder |
| Data9 | float | 8 | Y | The 9th value of the Data Recorder |
| Data10 | float | 8 | Y | The 10th value of the Data Recorder |
| Data11 | float | 8 | Y | The 11th value of the Data Recorder |
| Data12 | float | 8 | Y | The 12th value of the Data Recorder |
| Data13 | float | 8 | Y | The 13th value of the Data Recorder |
| Data14 | float | 8 | Y | The 14th value of the Data Recorder |
| Data15 | float | 8 | Y | The 15th value of the Data Recorder |
| Data16 | float | 8 | Y | The 16th value of the Data Recorder |
| Status | tinyint | 1 |  | The Status of the Data Recorder: |
|  |  |  |  | 1：Normal |
|  |  |  |  | 2：Invalid |
| Total |  | 143 |  |  |

- For meter datalog, # of Group = # of Data Recorder. The data recorders are pre-configured in the meter, the maximum of parameters for each data recorder is 16.

For virtual datalog: #of Group = Ceiling (# of Virtual Data Points / 16). Each group consists of 16 data points. For example, if there are 30 parameters required to do virtual datalog, parameter 1~16 will be in group 1, and parameter 17~30 will be in group 2.

- Interval is in minutes.

- For meter/virtual datalog, one parameter stored for 365 days, at a 5-minute interval, will approximately consume 1MB size.

- The formula to obtain the memory size growth of Energy Data is as follows –

Growth (MB) =

120 x #of Device x #of Energy Data Points x Running Days

(1024 x 1024)

Remarks:

- Each energy data point requires 120 bytes.

| PD_TB_05_YYYY: Energy Data |  |  |  |  |
| --- | --- | --- | --- | --- |
| Column Name | Data Type | Data Length (Byte) | Allow Nulls | Description |
| StationID | int | 4 |  | Station ID |
| EngMeasID | int | 4 |  | The ID of Energy Data Point |
| LogTime | datetime | 8 |  | The Log time of Energy Data Point |
| RtlVal | bigint | 8 | Y | The Real-time value for the Energy Data Point |
| SegVal1 | bigint | 8 | Y | The Daily Consumption value of Tariff 1 for the Energy Data Point |
| SegVal2 | bigint | 8 | Y | The Daily Consumption value of Tariff 2 for the Energy Data Point |
| SegVal3 | bigint | 8 | Y | The Daily Consumption value of Tariff 3 for the Energy Data Point |
| SegVal4 | bigint | 8 | Y | The Daily Consumption value of Tariff 4 for the Energy Data Point |
| SegVal5 | bigint | 8 | Y | The Daily Consumption value of Tariff 5 for the Energy Data Point |
| SegVal6 | bigint | 8 | Y | The Daily Consumption value of Tariff 6 for the Energy Data Point |
| SegVal7 | bigint | 8 | Y | The Daily Consumption value of Tariff 7 for the Energy Data Point |
| SegVal8 | bigint | 8 | Y | The Daily Consumption value of Tariff 8 for the Energy Data Point |
| SegVal9 | bigint | 8 | Y | The Daily Consumption value of Tariff 9 for the Energy Data Point |
| SegVal10 | bigint | 8 | Y | The Daily Consumption value of Tariff 10 for the Energy Data Point |
| DayVal | bigint | 8 | Y | The Daily Consumption value for the Energy Data Point |
| Monval | bigint | 8 | Y | The Monthly Consumption value for the Energy Data Point |
| Total |  | 120 |  |  |

- Each energy data point stores one record every day.

- For energy data, one parameter stored for 1 day, will approximately consume 120-byte size.

- The formula to obtain the memory size growth of SOE is as follows –

Growth (MB) =

1585 x #of Device x Occurrence

(1024 x 1024)

Remarks:

- Each event requires 1585 bytes.

| PD_TB_06_YYYY: SOE |  |  |  |  |
| --- | --- | --- | --- | --- |
| Column Name | Data Type | Data Length (Byte) | Allow Nulls | Description |
| ID | int | 4 |  | Event ID |
| EventTime | datetime | 8 |  | Event Time |
| Msec | int | 4 |  | Event Time (millisecond) |
| StationID | int | 4 |  | Station ID |
| ChannelID | int | 4 |  | Channel ID |
| DeviceID | int | 4 |  | Station ID |
| StationFlag | tinyint | 1 |  | Station Flag: Main/Standby |
| EventType | int | 4 |  | Event Type |
| EventByte | int | 4 |  | Event Type Secondary Classification |
| EventClass | int | 4 |  | Event Class |
| Code1 | int | 4 | Y | Event Original Information 1 |
| Code2 | int | 4 | Y | Event Original Information 2 |
| EveStr1 | nvarchar(256) | 512 | Y | Event Original Information 3 |
| EveStr2 | nvarchar(256) | 512 | Y | Event Original Information 4 |
| Description | nvarchar(256) | 512 |  | Event Description |
| Total |  | 1585 |  |  |

- One SOE will approximately consume 1KB size.

- The formula to obtain the memory size growth of Waveform is as follows –

Growth (MB) =

(#of Channel x 2 + 8) x Samples/Cycle x Cycles x #of Device x Occurrence

(1024 x 1024)

Remarks:

- Channel presents to V1, V2, V3, I1, I2, I3, …

- One waveform for V1, V2 & V3 @256samples/cycle x 20cycles will approximately consume 32KB size.